## Sheet1
Thermal Efficiency and Power Output of the plant at different cold and hot water inlet temperatures and ratios of hot water to cold water mass flowrates | [10 empty] | Thermal Efficiency and Power Output of the plant at different cold and hot water inlet temperatures, turbine inlet temperatures of the working fluid and mass flow rates of the hot fluid
5 deg CW
5 deg CW | [11 empty] | 0.1 |  |  | 0.15 |  |  | 0.2 |  |  | 0.25
| 30 |  | 40 |  | 50 |  | 60 |  | 70 |  | HWT | T1 | nth | Power | T1 | nth | Power | T1 | nth | Power | T1 | nth | Power
mHW/mCW | nth | Power | nth | Power | nth | Power | nth | Power | nth | Power | 30 | 24.5 | 1.3915 | 22.788 | 25.1 | 1.6511 | 27.008 | 25.6 | 1.8064 | 29.54 | 26.3 | 1.9639 | 32.072
0.4 | 1.3915 | 22.788 | 2.2126 | 35.448 | 3.2836 | 51.484 | 3.5215 | 54.016 | 3.8965 | 59.08 | 40 | 30.6 | 2.2126 | 35.448 | 31.1 | 2.3662 | 37.98 | 31.4 | 2.4711 | 39.668 | 31.7 | 2.576 | 41.356
0.6 | 1.6511 | 27.008 | 2.3662 | 37.98 | 3.4431 | 54.016 | 3.6314 | 55.704 | 3.951 | 59.924 | 50 | 38.8 | 3.2836 | 51.484 | 39.2 | 3.4431 | 54.016 | 39.5 | 3.5503 | 55.704 | 39.7 | 3.6039 | 56.548
0.8 | 1.8064 | 29.54 | 2.4711 | 39.668 | 3.5503 | 55.704 | 3.6831 | 56.548 | 4.2185 | 64.144 | 60 | 43.9 | 3.5215 | 54.016 | 44.2 | 3.6314 | 55.704 | 44.4 | 3.6831 | 56.548 | 44.9 | 3.7858 | 58.236
1 | 1.9639 | 32.072 | 2.576 | 41.356 | 3.6039 | 56.548 | 3.7858 | 58.236 | 4.3789 | 66.676 | 70 | 48.5 | 3.8965 | 59.08 | 48.7 | 3.951 | 59.924 | 49.2 | 4.2185 | 64.144 | 49.6 | 4.3789 | 66.676
8 deg CW | [11 empty] | 8 deg CW
| 30 |  | 40 |  | 50 |  | 60 |  | 70 |  |  | 0.1 |  |  | 0.15 |  |  | 0.2 |  |  | 0.25
mHW/mCW | nth | Power | nth | Power | nth | Power | nth | Power | nth | Power | HWT | T1 | nth | Power | T1 | nth | Power | T1 | nth | Power | T1 | nth | Power
0.4 | 1.2872 | 21.1 | 2.1505 | 34.604 | 3.2108 | 50.64 | 3.4627 | 53.172 | 3.6884 | 55.704 | 30 | 24.6 | 1.2872 | 21.1 | 25.2 | 1.4918 | 24.476 | 25.8 | 1.7523 | 28.696 | 26.4 | 1.8589 | 30.384
0.6 | 1.4918 | 24.476 | 2.2545 | 36.292 | 3.3328 | 52.328 | 3.5194 | 54.016 | 3.7968 | 57.392 | 40 | 30.7 | 2.1505 | 34.604 | 31.2 | 2.2545 | 36.292 | 31.5 | 2.3591 | 37.98 | 31.8 | 2.4693 | 39.668
0.8 | 1.7523 | 28.696 | 2.3591 | 37.98 | 3.4901 | 54.86 | 3.5761 | 54.86 | 4.0359 | 60.768 | 50 | 39 | 3.2108 | 50.64 | 39.3 | 3.3328 | 52.328 | 39.7 | 3.4901 | 54.86 | 39.9 | 3.5509 | 55.704
1 | 1.8589 | 30.384 | 2.4693 | 39.668 | 3.5509 | 55.704 | 3.732 | 57.392 | 4.1736 | 63.3 | 60 | 44.4 | 3.4627 | 53.172 | 44.6 | 3.5194 | 54.016 | 44.8 | 3.5761 | 54.86 | 45.3 | 3.732 | 57.392
[11 empty] | 70 | 48.5 | 3.6884 | 55.704 | 48.8 | 3.7968 | 57.392 | 49.3 | 4.0359 | 60.768 | 49.7 | 4.1736 | 63.3
11 deg CW
| 30 |  | 40 |  | 50 |  | 60 |  | 70 |  |  | 11 deg CW
mHW/mCW | nth | Power | nth | Power | nth | Power | nth | Power | nth | Power |  | 0.1 |  |  | 0.15 |  |  | 0.2 |  |  | 0.25
0.4 | 1.1855 | 19.412 | 2.0435 | 32.916 | 3.1356 | 49.796 | 3.3863 | 52.328 | 3.5607 | 54.016 | HWT | T1 | nth | Power | T1 | nth | Power | T1 | nth | Power | T1 | nth | Power
0.6 | 1.3412 | 21.944 | 2.1977 | 35.448 | 3.2417 | 51.484 | 3.4445 | 53.172 | 3.7264 | 56.548 | 30 | 24.9 | 1.1855 | 19.412 | 25.3 | 1.3412 | 21.944 | 25.9 | 1.5988 | 26.164 | 26.6 | 1.7534 | 28.696
0.8 | 1.5988 | 26.164 | 2.3021 | 37.136 | 3.3605 | 53.172 | 3.4961 | 54.016 | 3.9401 | 59.924 | 40 | 30.9 | 2.0435 | 32.916 | 31.3 | 2.1977 | 35.448 | 31.6 | 2.3021 | 37.136 | 32 | 2.4071 | 38.824
1 | 1.7534 | 28.696 | 2.4071 | 38.824 | 3.4162 | 54.016 | 3.6578 | 56.548 | 4.0952 | 62.456 | 50 | 39.1 | 3.1356 | 49.796 | 39.4 | 3.2417 | 51.484 | 39.6 | 3.3605 | 53.172 | 39.9 | 3.4162 | 54.016
[11 empty] | 60 | 44.8 | 3.3863 | 52.328 | 44.9 | 3.4445 | 53.172 | 45.1 | 3.4961 | 54.016 | 45.5 | 3.6578 | 56.548
[11 empty] | 70 | 48.6 | 3.5607 | 54.016 | 48.8 | 3.7264 | 56.548 | 49.2 | 3.9401 | 59.924 | 49.8 | 4.0952 | 62.456